MANTHINK  /  INDUSTRIAL IoT

GD73

LoRaWAN Gateway

Standardized Device Manual

| VERSION Current | DOCUMENT Device Manual |
| --- | --- |

Revision History

| Version | Change Description |
| --- | --- |
| Current | Current published version |

DOCUMENT NAVIGATION

Contents

1. Product Description	4

2. Main Features	4

3. Technical Specifications	4

4. Accessories	8

5. Product Dimensions	8

6. Interface Description	9

7. Indicator Description	10

8. Product Model	10

8.1 Standard Model	10

8.2 Model Components	10

9. Gateway Installation	11

10. Accessory Connections	11

10.1 Antenna Connection	11

10.2 Type-C Power Connection	11

10.3 Network Cable Connection	11

10.4 SIM Card Installation	11

10.5 RS485 Connection	11

10.6 DC 5–24 V Power Connection	12

11. Gateway Mounting	12

11.1 DIN-Rail Mounting	12

12. Gateway Configuration	12

13. RS485 Use	12

14. Platform Connections	12

15. Security Configuration Recommendations	12

16. Contact Us	13

# 1. Product Description

GD73 is an indoor, multi-channel, high-performance gateway designed by ManThink for LoRaWAN systems. It uses a high-performance processor, a Semtech SX1302 LoRa concentrator and an industrial-grade Wi-Fi module. It supports Ethernet, cellular, Wi-Fi access-point/client, Bluetooth Low Energy (BLE) and RS485 connections. The aluminum-alloy enclosure supports DIN-rail mounting and PoE, USB Type-C or DC 5–24 V power. GD73 is suitable for campuses, buildings, industrial sites, smart-property deployments and other indoor IoT environments.

# 2. Main Features

- High-performance chipset, at least 512 MB DDR and at least 16 GB eMMC

- Semtech SX1302 LoRa concentrator with at least 8 LoRaWAN uplink channels, 8 frequency points and 16 demodulators

- -141 dBm LoRa receiver sensitivity at SF12/BW 125 kHz; maximum transmit power is 27 dBm for suffix -1 and 22 dBm for suffix -2, with a maximum-power tolerance of ±2 dBm

- Standard LoRaWAN and AS923 regional parameters, plus regional configurations for CN470, EU433, EU868, AU915 and US915

- Industrial-grade Wi-Fi module supporting access-point and client modes

- 2.4 GHz or 5 GHz Wi-Fi, IEEE 802.11a/b/g/n, at least 100 Mbps download and at least 50 Mbps upload

- Bluetooth Low Energy (BLE)

- RS485 interface for industrial meters, controllers and other field equipment

- Ethernet, 4G/LTE and Wi-Fi backhaul, plus dual-gateway redundancy architecture

- GPS and BeiDou (BDS) positioning, plus NTP clock synchronization

- MQTT, MQTTS, HTTP, HTTPS, SNMP, DHCP, static IP, NAT and ICMP

- WPA2, AES, TLS, firewall and access control list (ACL)

- Secure remote management, configuration and upgrades; supports Python and Node-RED for secondary development

- Automatic fault detection and recovery; monitoring of CPU, memory, storage, network and LoRa communication quality

- PoE, USB Type-C and DC 5–24 V power, with visual configuration and maintenance through gwTool7

# 3. Technical Specifications

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| COMPUTE AND STORAGE |  |  |
|  | SoC | High-performance multi-core processor |
|  | Memory | DDR, ≥ 512 MB |
|  | Storage | eMMC, ≥ 16 GB |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| SOFTWARE AND PLATFORM |  |  |
|  | Built-in platform | Built-in TKL LoRaWAN network server and IoT platform |
|  | External platforms/protocols | ThinkLink, ChirpStack, TTN, Basic Station and GWMP |
|  | Data services | PostgreSQL, Redis, historical data storage, Thing Model, application data parsing and Dashboard |
|  | Secondary development | Supports Python and Node-RED |
|  | Remote operations | Remote management, configuration and upgrades over SSH |
|  | Fault handling | Automatic fault detection and recovery |
|  | Monitoring | Reporting of CPU, memory and storage usage, network status and LoRa communication quality |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| LORAWAN |  |  |
|  | Concentrator | Semtech SX1302 |
|  | Protocol | Standard LoRaWAN; compliant with LoRa Alliance™ LoRaWAN Specification v1.0.4 or a later version |
|  | Operating bands | AS923: 920–928 MHz; regional configurations also include CN470, EU433, EU868, US915 (902–928 MHz) and AU915 |
|  | Channels/frequency points | At least 8 uplink channels; 8 frequency points at BW = 125 kHz |
|  | Demodulators | 16, processing up to 16 packets simultaneously |
|  | Demodulator composition | 8 × SF5–SF12 LoRa®demodulators; 8 × SF5–SF10 LoRa®demodulators |
|  | Channel capacity | 65 logical channels; each SF, bandwidth and frequency-point combination defines a channel |
|  | Communication rate | 292 bps to 15.625 kbps |
|  | Spreading factors | SF5 to SF12 |
|  | Single-channel bandwidth | 125 kHz or higher |
|  | Operating mode | Half-duplex |
|  | Transmit power | Suffix -1: 27 dBm maximum; suffix -2: 22 dBm maximum; maximum-power tolerance: ±2 dBm; projects requiring at least 25 dBm capability shall select suffix -1 |
|  | Receiver sensitivity | -141 dBm at SF12/BW 125 kHz |
|  | Antenna | Omnidirectional LoRa antenna |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| WI-FI AND BLUETOOTH |  |  |
|  | Wi-Fi module | Industrial-grade Wi-Fi module |
|  | Operating modes | Access-point mode and client mode |
|  | Bands/standards | 2.4 GHz or 5 GHz; IEEE 802.11a/b/g/n |
|  | Download/upload | Download ≥ 100 Mbps; upload ≥ 50 Mbps |
|  | Security | WPA2, AES and TLS |
|  | Bluetooth | Bluetooth Low Energy (BLE) |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| NETWORK AND TRANSPORT |  |  |
|  | Ethernet | 1000M/100M; DHCP and static IP configuration |
|  | Cellular uplink | CAT1 4G/LTE module by default; LTE-FDD B1/3/5/8 and LTE-TDD B34/38/39/40/41 |
|  | Data forwarding | MQTT, MQTTS, HTTP and HTTPS |
|  | Network services | NTP, prevailing-version SNMP, NAT and ICMP diagnostics |
|  | Network redundancy | Dual-gateway architecture for network redundancy |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| SECURITY AND AUTHENTICATION |  |  |
|  | Device identity | IMEI or device-feature-string authentication |
|  | Access protection | Firewall and access control list (ACL) |
|  | Transport security | Prevailing-version TLS; administrators can disable unsafe SSH/TLS cipher suites |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| PORTS AND TIMING |  |  |
|  | Configuration ports | USB Type-C, Ethernet and Wi-Fi |
|  | SIM slot | One external SIM slot supporting LTE/5G SIM cards; cellular standards are determined by the configured module |
|  | Positioning/timing | GPS and BeiDou (BDS) positioning; NTP synchronization |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| RS485 |  |  |
|  | Physical interface | One RS485 interface on green A/B terminals |
|  | Connection | Half-duplex differential bus for industrial meters, controllers and other field equipment |
|  | Communication parameters | Baud rate, parity and application protocol are set in the device configuration or application |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| POWER |  |  |
|  | PoE power | One PoE Ethernet port; nominal 48 V PoE |
|  | USB power | USB Type-C, 5 V |
|  | DC power | DC 5–24 V on green V−/V+ terminals |
|  | Power consumption | ≤ 5 W in a typical configuration |

| Category | Parameter | GD73 Specification |
| --- | --- | --- |
| ENVIRONMENT AND ENCLOSURE |  |  |
|  | Operating temperature | -20°C to 65°C |
|  | Operating humidity | 0% to 95% RH, non-condensing |
|  | Ingress protection | IP53, meeting the IP30-or-better indoor-gateway requirement |
|  | Radio-equipment requirement | Compliant with HKCA 1078 requirements |
|  | Weight | 0.33 kg |
|  | Dimensions | 139 × 122 × 28 mm |
|  | Installation | DIN-rail mounting |

Cellular deployment note: if local operator bands are outside the default module range, contact ManThink for a suitable cellular module. Configure actual LoRa transmit power to comply with local regulations.

# 4. Accessories

The product package includes the GD73 gateway, PoE power components, power adapter, Type-C cable, DIN-rail backplate, LoRa antenna, LTE antenna, positioning antenna, Wi-Fi antenna, network cable, green terminal block and mounting fasteners. Cellular-enabled versions include an LTE/5G SIM card with a data plan suitable for the project transmission requirements.

# 5. Product Dimensions

The product outline and installation dimensions are shown below.

Figure  GD73 product dimensions

# 6. Interface Description

| Interface | Description |
| --- | --- |
| WiFi | Wi-Fi antenna interface |
| TF | Memory-card slot |
| LoRa | LoRa antenna interface |
| B / A | RS485 differential-signal terminals |
| V− / V+ | DC 5–24 V power-input terminals |
| RST | Reset button |
| SIM | SIM-card slot |
| RJ45 | Ethernet and PoE power interface |
| PWR | USB Type-C power interface |
| 4G | LTE antenna interface |

# 7. Indicator Description

| Indicator | State | Description |
| --- | --- | --- |
| Run indicator | Steady / off / 1 Hz flashing | System starting / base startup complete and applications starting / normal operation |
| Network indicator | 1 Hz / 500 ms / rapid flashing | Network normal / network abnormal / network configuration in progress |
| Cellular indicator | Off / steady / irregular flashing | No module / module installed without SIM / cellular data activity |
| LoRa transceiver indicator | TX-color / RX-color flashing | Transmitting / receiving LoRa packets |
| LAN status indicator | Red / blue | System-control state / Wi-Fi connection state |
| Fault indicator | Rapid flashing / off / flashing | Startup phase 2 / no fault / fault detected |

# 8. Product Model

## 8.1 Standard Model

The GD73 standard model is GD738-AG-AS923-N-2.

## 8.2 Model Components

- GD738: series and RF band. GD73 identifies the indoor LoRaWAN gateway series; 8 identifies the 800 MHz-and-above RF version.

- -AG: LoRa architecture and cellular configuration. A identifies one LoRa antenna, 8 frequency points, 65 channels and half-duplex operation; G identifies an integrated cellular module.

- -AS923: LoRaWAN regional standard. Identifies support for AS923 regional parameters.

- -N: version code. N identifies the default version; other values are used for customized versions.

- -1: transmit-power version. Maximum transmit power is 27 dBm, with a maximum-power tolerance of ±2 dBm.

- -2: transmit-power version. Maximum transmit power is 22 dBm, with a maximum-power tolerance of ±2 dBm.

# 9. Gateway Installation

Do not open the gateway enclosure during installation. Disconnect power first and verify that antennas, PoE, DC power and site cabling meet deployment requirements.

# 10. Accessory Connections

## 10.1 Antenna Connection

- Connect the LoRa, LTE, positioning and Wi-Fi antennas to their matching interfaces.

- Tighten antenna connectors evenly without overtightening.

## 10.2 Type-C Power Connection

- The Type-C power cable is not required when PoE or DC power is used.

- For USB power, connect the Type-C cable to the gateway PWR interface.

## 10.3 Network Cable Connection

- Connect the network cable to the gateway RJ45 interface.

- When using PoE, connect the other end to compliant PoE equipment.

## 10.4 SIM Card Installation

- Before using cellular networking, insert a SIM card into the gateway SIM slot.

- Follow the slot marking for contact and notch orientation; do not force the card.

## 10.5 RS485 Connection

- With power disconnected, connect the field-device RS485 A and B wires to the matching green A and B terminals.

- Verify bus polarity, termination and common-reference requirements against the field-device manual.

- After power-up, configure matching baud rate, data bits, stop bits, parity and application protocol in the application or device configuration.

## 10.6 DC 5–24 V Power Connection

- With power disconnected, connect the supply negative and positive wires to the green V− and V+ terminals.

- Verify the voltage range and polarity before applying power.

# 11. Gateway Mounting

## 11.1 DIN-Rail Mounting

- Fasten the DIN-rail backplate to the rear of the gateway.

- Engage the backplate with the matching DIN rail and verify that the gateway is secure.

# 12. Gateway Configuration

GD73 is configured and maintained with gwTool7. See the gwTool7 Gateway Administrator Manual.

# 13. RS485 Use

The RS485 interface connects field meters, sensors or controllers. After wiring and power-up, configure serial parameters and the application protocol in the GD73 application or protocol-conversion program to match the slave device. For long buses, follow the site topology when configuring termination, biasing, shielding and grounding, and avoid star branches that can cause signal reflections.

# 14. Platform Connections

- ThinkLink: ThinkLink User Guide

- ChirpStack: Connect with Basic Station (gwTool7)

- TTN: Connect with Basic Station (gwTool7)

# 15. Security Configuration Recommendations

- Change default administrative credentials during initial deployment, restrict management access to trusted networks, enable the firewall or ACL, and disable unnecessary services and ports.

- Use a prevailing TLS version and disable unsafe SSH/TLS cipher suites; retain audit records for remote upgrades, configuration changes and administrator operations, and regularly review CPU, memory, storage, network and LoRa communication-quality alarms.

# 16. Contact Us

Website: www.manthink.cn · Email: info@manthink.cn · Tel: +86 15810684257