MANTHINK  /  INDUSTRIAL IoT

KC11

LoRaWAN EB Collector

Standardized Device Manual

| VERSION 1.0 | DOCUMENT Device Manual |
| --- | --- |

Revision History

| Version | Change Description |
| --- | --- |
| 1.0 | Current published version |

Contents

1. Product Description

2. Application areas

3. Main features

4. Parameters

5. Dimensions and Interfaces

5.1 DIimensions

5.2 Interface Definition

6. Product Model

6.1 Model example

6.2 Model component breakdown

6.3 Complete model meaning

7. Network topology

8. Working mode

8.1 EB configure collection and upload tasks

8.2 Communication Test

8.3 network access

9. Installation Instructions

10. Standard

11. Parameter Modification

11.1 Configuration Parameter Address Table

12. ThinkLink Thing Model

12.1 Device Template

13. Contact Us

# 1. Product Description

KC11 is a high-performance, low-power, highly configurable data transmission unit (DTU) independently developed by ManThink . Product Integration High Performance MCU and LoRa®RF chip, based on LoRa®Wireless technology, supports standard LoRaWAN®Protocol, which has the advantages of long communication distance, strong signal penetration and low power consumption.

KC11 adopts industrial-grade guide rail design, supports 100V-230V AC wide voltage power supply, and is suitable for all kinds of industrial field environment. Through the RS-485 interface, external devices can be easily connected, data collection and remote control can be realized, and business data can be stably uploaded to the application platform through the LoRaWAN network.

The product is compatible with ManThink and third-party LoRaWAN®The Gateway also supports access to  IoT platforms such as ThinkLink, ChirpStack, and The Things Network(TTN). It has excellent system integration capabilities.

KC11 has a built-in EB virtual machine, which supports the generation of firmware through EB script compilation and remote deployment through FUOTA (Firmware Over-the-air upgrade). With the help of EB virtual machine, users can flexibly realize protocol analysis and docking of RS-485 equipment, and complete core business logic processing such as COV (change value reporting), alarm triggering, data reorganization, etc. on the terminal side, thus significantly improving the response efficiency and intelligence level of the system.

# 2. Application areas

Industrial Site

Electric meter reading

Hydrometeorological monitoring

Environmental protection, municipal and other related scene monitoring

# 3. Main features

Support RS-485 interface

AC 85V-270V power supply

Support for EB virtual machines

Support remote upgrade via LoRaWAN communication

Support ThinkLink/ChirpStack/TTN platform docking

Support US902,AU915,AS923,EU868,EU433,CN470 LoRaWAN standards

Compatible with all RS-485-based communication protocols

# 4. Parameters

| Interface | joint Type | 2.54mm Terminal |
| --- | --- | --- |
|  | wiring quantity | 4 |
|  | display | 4 indicator lights, RU,LR,TX,RX |

| Item | Value |
| --- | --- |
| WIRELESS PARAMETERS |  |
| Protocol | standard LoRaWAN |
| regional Standards | CN470/EU433/EU868/AS923/AU915/Us902 |
| transmit power | maximum Support 22dBm ( can be changed) |
| receiving sensitivity | -142dBm(SF=12,BW=125kHz) |
| Working mode | OTAA/ABP Class C |

| Item | Value |
| --- | --- |
| CONFIGURATION |  |
| test /Trigger mode | press the button 2 seconds to trigger heartbeat data > 6 seconds to trigger the network |
| parameter configuration | by NS issue instruction |

| Item | Value |
| --- | --- |
| PHYSICAL CHARACTERISTICS |  |
| power supply mode | AC 85V-270V |
| receiving current | <8mA |
| emission current | <110mA (22dBm transmit power) |
| working temperature | -40°C ~85°C |
| relative humidity | ≤ 95% (no condensation) |
| protection level | IP53 |
| Material &Color | ABS + PC, White |
| dimensions | 89.2mm x 35.8mm x 65.4mm |
| installation method | DIN rail |

# 5. Dimensions and Interfaces

## 5.1 DIimensions

## 5.2 Interface Definition

Figure  5.2 Interface Definition

| Name | Definition |
| --- | --- |
| N | 80-270V AC power supply zero line |
| L | 80-270V AC power supply live wire |
| 485A | 485A |
| 485B | 485B |
| 120Ω; | matching resistor, bus equipment is more, the distance is far, when there is interference, this terminal and RS485A short circuit |
| INT | I/O input |
| GND | GND |
| 12V + | keep interface, please keep hanging |
| trigger button | click this button, KC11 will query the data and upload |
| long press the button for more than 6 seconds, will trigger the network |  |
| RU | The system operation indicator flashes once per second, indicating that the system is operating normally |
| LR | status indicator, flashing for 100ms when data is sent and received |
| TX | data transmission indicator, send flashing while RS-485 data |
| RX | data reception indicator, blinking when receiving RS-485 data |

# 6. Product Model

## 6.1 Model example

KC118-A1-AS923-N

## 6.2 Model component breakdown

KC118: product series and RF band.

KC11 identifies a second-generation DIN-rail RS-485 DTU.

8 identifies the 800 MHz-and-above RF version for EU868, AS923, AU915 and US902.

Other band option: 4 identifies the 400 MHz RF version for EU433 and CN470.

-A1: hardware and power configuration.

A identifies the default hardware configuration.

1 identifies an AC 85–270 V power input.

-AS923: LoRaWAN regional standard.

AS923 means that the device supports the LoRaWAN AS923 regional parameters.

Other regional codes are CN470, EU433, EU868, AU915 and US902; US902 denotes the LoRaWAN US915 (902–928 MHz) regional parameters.

-N: default version.

N identifies the default version.

Other values are reserved for customized or special versions.

## 6.3 Complete model meaning

The complete meaning of KC118-A1-AS923-N is:

This is a second-generation DIN-rail RS-485 DTU in the 800 MHz-and-above RF class. It uses the default hardware configuration, accepts AC 85–270 V input, supports the LoRaWAN AS923 regional standard, and uses the default final version code N.

# 7. Network topology

KC11 is a standard LoRaWAN device, KC11 normal operation requires LoRaWAN network support. You can use the LoRaWAN gateway of ManThink or a third-party LoRaWAN gateway with the support of LoRaWAN NS. KC11 supports access to standard LoRaWAN networks such as ThinkLink, Chirp stack, and TTN. You can use the ThinkLink configuration model to implement business functions, card view presentation, and other business logic.

The LoRaWAN network topology is as follows:

Figure  7. Network topology

# 8. Working mode

## 8.1 EB configure collection and upload tasks

KC11 has a built-in EB virtual machine, which can implement various business logic of meter reading by calling SDK and TS code. EB instructions for use:

\AN-25100101 EB compiler SDK instructions

## 8.2 Communication Test

Short press the button to trigger a packet of upstream measurement data

## 8.3 network access

6 long press the button 6s-8s, you can trigger a packet of network data.

# 9. Installation Instructions

FIXED EQUIPMENT:clipping the DTU into the guide rail.

Connect the power supply:correctly connect the neutral and live wires to the power terminals marked "N" and "L.

Wiring communication:connect the "A" and "B" terminals of your RS485 device to the "485-A" and "485-B" terminals of the DTU respectively.

Power-on operation:turn on the power supply, observe the status of the indicator light, and start communication after the indicator light indicates stably.

Note:please make sure that the power is disconnected before wiring, and all serial port parameters need to match your terminal equipment.

Figure  9. Installation Instructions

# 10. Standard

The format of the communication protocol is customized through EB Compilation. We recommend that you use the protocol format standard recommended by ManThink.

\PTL-D01 ManThink Technology IoT Terminal Application Layer General Protocol V1.5

# 11. Parameter Modification

Refer to Chapter 5 of PTL-D01-Internet of Things Terminal Application Layer General Protocol V1.3 for parameter modification. Parameter modification is delivered through Port 214.

\PTL-D01 ManThink Technology IoT Terminal Application Layer General Protocol V1.5

## 11.1 Configuration Parameter Address Table

\AN-25100106 EdgeBus App Parameter Manual

# 12. ThinkLink Thing Model

Log in to <https://thinklink.manthink.cn>

## 12.1 Device Template

Add devices according to the template MT-EB-POWER. The models already mounted under MT-EB-POWER are as follows:

Thing Model: MT-EB

RPC:

\[MT ACT\] action: Used to execute operations such as reset, join, redo, and reading parameters

\[MT ACT\] transparent: Transparent RPC; hexadecimal data can be sent via port 51, which will be forwarded to sub-devices through the RS485 interface, and responses from the sub-device will be returned

\[MT SET\] app para: Set EB parameters

\[MT ACT\] debug modbus: Online Modbus debugging by entering information such as 485 address and Modbus function code

ALARM: Used for alarm functionality; trigger rules must be configured to enable full alarm features

# 13. Contact Us

Website: www.manthink.cn

Email:  info@ manthink.cn

Tel: +86-15810684257