MANTHINK  /  INDUSTRIAL IoT

KS51

LoRaWAN Sensor

Standardized Device Manual

| VERSION 当前版本 | DOCUMENT Device Manual |
| --- | --- |

# Product Description

KS51 is a wireless water leakage detector sensor device, which monitors whether there is a water leakage event in the area monitored by the probe in real time through the sensor. When a water leakage event occurs, the alarm information is triggered and transmit to the application platform through LoRa signal.

KS51 periodically sends heartbeat information to ensure that the application platform monitors the  status of the device in real time. The default configuration period is 3 hours. The user can set the sampling period and the heartbeat period through the palm machine or the management platform.

Supports LoRaWAN and LinkWAN protocols, IP65 protection level.

KS51 through real-time monitoring of flooding events, and alarm, the first time to inform the management of the flooding site for timely treatment, for storage, warehouse, factory and other events to protect, to avoid the loss of goods or equipment due to flooding events.

KS51 based on LoRa®Wireless technology, supports standard LoRaWAN®Networking communication has the characteristics of long communication distance and low power consumption. The product has 4 built-in 2700 mAh large-capacity lithium battery, the battery life is  more than 8 years.

KS51  support with ManThink/3rd party LoRaWAN gateway, is combined with the ThinkLink/Chirp stack/TTN third-party Internet of Things platform to realize point-type and rope-type interfaces.

KS51 has a high protection level of IP65, which can be widely applied to the management requirements of smart industries, smart buildings and other scenarios.

# Application Areas

Warehousing and warehouse of logistics

Data Center and Service Room

Unattended factory, workshop

Smart Home, Smart Building

# Key Features

Low battery voltage alarm

Equipment failure alarm

Support ThinkLink platform operation and maintenance

LoRa modulation, receiving sensitivity up to-139dBm

Standby power consumption <5uA

High energy density lithium battery, to ensure that the product has a continuous working life of 8 years (3 hours heartbeat cycle)

Support US902,AU915,AS923,EU868,EU433,CN470 LoRaWAN standard.

# Specifications

| Item | Value |
| --- | --- |
| INTERFACE |  |
| Connect Type | PG7, point/rope |
| Number of interfaces | 1 |
| Display | None |

| Item | Value |
| --- | --- |
| WIRELESS PARAMETERS |  |
| Communication Protocol | Standard LoRaWAN®Agreement |
| Regional Standards | CN470/EU433/EU868/AS923/AU915/Us902 |
| Transmit Power | Maximum Support 22dBm ( can be changed) |
| Receiving sensitivity | -142dBm(SF=12,BW=125kHz) |
| Working mode | OTAA/ABP Class A |

| Item | Value |
| --- | --- |
| CONFIGURATION |  |
| Test /Trigger mode | The magnet 2 seconds trigger heartbeat data 6 seconds trigger into the network |
| Parameter configuration | By NS issue instruction |

| Item | Value |
| --- | --- |
| PHYSICAL CHARACTERISTICS |  |
| Power supply | 4*2700 mAh ER14505 lithium battery |
| Sleep current | <5uA (25 ℃ at room temperature) |
| Emission current | <110mA (22dBm transmit power) |
| Battery life | 8 years (3 hours heartbeat cycle, 25 ℃ at room temperature) |
| Working temperature | -40°C ~85°C |
| Relative humidity | ≤95% (no condensation) |
| Protection level | IP65 |
| Material & Color | ABS + PC, White |
| Dimensions | 120mm * 72mm * 28mm |
| Installation method | Wall Hanging |

# Dimensions and Interfaces

Figure  Dimensions and Interfaces

| No. | Interface |
| --- | --- |
| 1 | LoRa antenna interface |
| 2 | Point/rope sensor interface |

# Product Model

## Model example

KS518-A1-AS923-N

## Model component breakdown

KS518: product series and RF band.

KS51 identifies a second-generation IP65 water-leak sensor.

8 identifies the 800 MHz-and-above RF version for EU868, AS923, AU915 and US902.

Other band option: 4 identifies the 400 MHz RF version for EU433 and CN470.

-A1: sensor type and power configuration.

A identifies point water-leak detection.

Other sensor option: B identifies rope water-leak detection.

1 identifies a built-in 10800 mAh battery.

Other power option: 2 identifies external DC 5–24 V input.

-AS923: LoRaWAN regional standard.

AS923 means that the device supports the LoRaWAN AS923 regional parameters.

Other regional codes are CN470, EU433, EU868, AU915 and US902; US902 denotes the LoRaWAN US915 (902–928 MHz) regional parameters.

-N: default version.

N identifies the default version.

Other values are reserved for customized or special versions.

## Complete model meaning

The complete meaning of KS518-A1-AS923-N is:

This is a second-generation IP65 point water-leak sensor in the 800 MHz-and-above RF class. It includes a 10800 mAh battery, supports the LoRaWAN AS923 regional standard, and uses the default final version code N.

# Instructions for use

# Network topology

KS51 is a standard LoRaWAN device, KS51 normal operation requires LoRaWAN network support. You can use the LoRaWAN gateway of ManThink or the LoRaWAN gateway of a third party, and it needs the support of LoRaWAN NS. KS51 supports accessing standard LoRaWAN networks such as ThinkLink, Chirp stack, and TTN. You can use the ThinkLink configuration model to implement business functions, card view presentation, and other business logic.

The LoRaWAN network topology is as follows:

Figure  Network topology

# Working mode

## Condition monitoring

KS51 continuously monitors the water leakage status,

Upload alarm information after leakage event.

After transmit the alarm information, enter the protection mechanism and no alarm will be given within 1 minute.

1 minute after the alarm, the detection probe level status will upload information again if there is no water leakage

NOTE It is impossible to detect the leakage state of non-conductive liquids, such as organic solvents, purified water, etc.

## Periodic heartbeat

The format of the heartbeat protocol is the same as that of the heartbeat trigger protocol, and the heartbeat period can be set by issuing instructions through NS.

## Communication Test

Use a magnet to stick a two-dimensional code on KS51 to trigger 2s-4S, which can trigger a packet of upstream measurement data.

## Network access

Use a magnet to stick a two-dimensional code on KS51 to trigger 6s-8s, which can trigger a packet of network access data.

# Installation Instructions

## Single point type water immersion installation diagram

Figure  Single point type water immersion installation diagram

① Hang the water detector sensor vertical wall on the wall, and the back of the water leakage sensor is installed with a back plate for fixing.

② Tighten the LoRa antenna

③ The root of the water immersion probe shall be closely attached to the wall surface with double-sided adhesive, and the height from the ground shall be 10cm.

NOTE Please ensure that the installation is covered by the Gateway when leakage

## Rope type water immersion installation diagram

Figure  Rope type water immersion installation diagram

① Hang the water leakage vertical wall on the wall, and the back of the water leakage sensor is equipped with a back plate for fixing.

② Tighten the LoRa antenna

③ Water leakage detection extension rope

preparation tools: Impact drill, drill bit, Phillips screwdriver, Buckle

use an electric drill to drill holes in the installation position in advance. The left and right sides of the water leakage detector will be equipped with installation holes, which will be fixed by screws. Then connect the extension cord, and use the buckle to fix the extension cord at the position where the water leakage needs to be monitored.

# Communication Protocol

# According to the standard

\PTL-D01 ManThink Technology IoT Terminal Application Layer General Protocol V1.5

# Data Items and Identifiers

LoRaWAN port number = 11

KS51 supports only one data format and sends data periodically according to a set period. When a flooding event occurs, it triggers one frame of uplink data.

Example (hex):82 21 12 00 F1 50 06

| Number | Data Item | Example | Start Address | Length | Description |
| --- | --- | --- | --- | --- | --- |
| 1 | Version number | 0x82 | 0 | 1 byte | Fixed at 0x82 |
| 2 | Control word | 0x21 | 1 | 1 byte | Fixed at 0x21 |
| 3 | Identifier | 0x12 | 2 | 1 byte | Fixed at 0x12 |
| 4 | Status | 0x00 | 3 | 1 byte | 0x00: dry; 0x01: water detected |
| 5 | Battery voltage | 0xF1 | 4 | 1 byte | Actual value = sample × 1.6 / 254 + 2 V |
| 6 | RSSI | 0x50 | 5 | 1 byte | Actual value = reported value - 160 dBm |
| 7 | SNR | 0x06 | 6 | 1 byte | uint8, unit: dB |

# ThinkLink reference model

Log in to <https://thinklink.manthink.cn>\n○ Search for KS51 in the model menu\n○ add using template KS51

# Parameter modification

\PTL-D01 ManThink Technology IoT Terminal Application Layer General Protocol V1.5

## Configuration parameter address table

| Number | data Item | default Value | start Address | length | description |
| --- | --- | --- | --- | --- | --- |
| 1 | upload period | 900 | 40 | 4 bytes | upload period, in seconds |

# Contact Us

Website: www.manthink.cn

Email: info@manthink.cn

Tel: +86 15810684257